## Sheet1
| WHRB#1 | WHRB#2 | WHRB#3 | WHRB#4
Steam Temp. | 349 | 347 | 266 | 347
Steam Pressure | 15.1 | 15.21 | 15.16 | 14.86
Steam Flow | 9.31 | 9.69 | 9.83 | 18.96
Feed water Temp. | 160 | 160 | 160 | 160
Feed water press. | 25 to 26 kg/cm²
Enthalpy of Steam (kcal/kg) | 753 | 751 | 708 | 752
Enthalpy of Feed water (kcal/kg) | 161 | 161 | 161 | 161
Flue gas flow( M³/hr) | 234784 | 359802 | 278120 | 679047
flue gas density | 0.54 | 0.52 | 0.54 | 0.52
Sp. Heat of flue gas | 0.24 | 0.24 | 0.24 | 0.24
Flue gas inlet temp. °C | 406 | 393 | 372 | 382
Flue gas outlet temp. °C | 234 | 235 | 223 | 226
Total heat input in boiler(kcal/hr) | 5233617.1008 | 7094719.7568 | 5370608.448 | 13220230.2336
heat out from boiler | 5511520 | 5717100 | 5377010 | 11205360
boiler effiency | 105.31 | 80.5825 | 100.1192 | 84.7592
WHRB#5
Steam Temp. | 331 |  |  |  | 4000
Steam Pressure | 15.09
Steam Flow | 12.21
Feed water Temp. at Eco. inlet | 130
Feed water Temp. at Eco. Out let | 160
Feed water press. | 25 to 26 kg/cm²
Enthalpy of Steam (kcal/kg) | 743
Enthalpy of Feed waterat Eco. inlet (kcal/kg) | 131
Enthalpy of Feed water at Eco. Outlet (kcal/kg) | 161
| Duct- 1 | Duct- 2
Flue gas flow( M³/hr) | 371663 | 40858
flue gas density | 0.48 | 0.42
Sp. Heat of flue gas | 0.24 | 0.24
Flue gas temp. °C I/L | 349 | 349
Flue gas temp. °C O/L | 93 | 93
Total heat input in boiler(kcal/hr) | 10960787.8656 | 1054332.5184
heat out from boiler | 10872030
boiler effiency | 90.4862

## Sheet2
| WHRB#1 | WHRB#2 | WHRB#3 | WHRB#4
Steam Temp. | 345 | 350 | 342 | 344
Steam Pressure | 15.1 | 15.21 | 15.16 | 14.86
Steam Flow | 9.31 | 9.69 | 9.83 | 18.96
Feed water Temp. | 160 | 160 | 160 | 160
Feed water press. | 25 to 26 kg/cm²
Enthalpy of Steam (kcal/kg) | 750.2392 | 752.8708 | 748.8038 | 750
Enthalpy of Feed water (kcal/kg) | 161 | 161 | 161 | 161
Flue gas flow( M³/hr) | 234784 | 359802 | 278120 | 679047
flue gas density | 0.54 | 0.52 | 0.54 | 0.52
Sp. Heat of flue gas | 0.24 | 0.24 | 0.24 | 0.24
Flue gas inlet temp. °C | 406 | 393 | 372 | 382
Flue gas outlet temp. °C | 234 | 235 | 223 | 226
Total heat input in boiler(kcal/hr) | 5233617.1008 | 7094719.7568 | 5370608.448 | 13220230.2336
heat out from boiler | 5485817.2727 | 5735228.1818 | 5778111.6268 | 11167440
boiler effiency | 104.8189 | 80.838 | 107.5877 | 84.4724
WHRB#5
Steam Temp. | 331
Steam Pressure | 15.09
Steam Flow | 12.21
Feed water Temp. at Eco. inlet | 130
Feed water Temp. at Eco. Out let | 160
Feed water press. | 25 to 26 kg/cm²
Enthalpy of Steam (kcal/kg) | 743
Enthalpy of Feed waterat Eco. inlet (kcal/kg) | 131
Enthalpy of Feed water at Eco. Outlet (kcal/kg) | 161
| Duct- 1 | Duct- 2
Flue gas flow( M³/hr) | 371663 | 40858
flue gas density | 0.48 | 0.42
Sp. Heat of flue gas | 0.24 | 0.24
Flue gas temp. °C I/L | 349 | 349
Flue gas temp. °C O/L | 93 | 93
Total heat input in boiler(kcal/hr) | 10960787.8656 | 1054332.5184
heat out from boiler | 10872030
boiler effiency | 90.4862

## Sheet3
Based on design Parameters
| WHRB#1 | WHRB#2 | WHRB#3 | WHRB#4
Steam Temp. | 325 | 325 | 325 | 325
Steam Pressure | 18 | 18 | 18 | 18
Steam Flow | 10 | 12.94 | 9.1 | 20.6
Feed water Temp. | 130 | 130 | 130 | 130
Feed water press. | 25 to 26 kg/cm²
Enthalpy of Steam (kcal/kg) | 738 | 738 | 738 | 738 | 3086 | 546
Enthalpy of Feed water (kcal/kg) | 131 | 131 | 131 | 131 | 738.2775 | 130.622
Flue gas flow(N M³/hr) | 100000 | 137000 | 111000 | 250000
flue gas density | 1.4 | 1.4 | 1.4 | 1.4
Sp. Heat of flue gas | 0.24 | 0.24 | 0.24 | 0.24
Flue gas inlet temp. °C | 400 | 385 | 365 | 365
Flue gas outlet temp. °C | 240 | 241 | 240 | 240
Total heat input in boiler(kcal/hr) | 5376000 | 6628608 | 4662000 | 10500000
heat out from boiler | 6070000 | 7854580 | 5523700 | 12504200
boiler effiency | 112.9092 | 118.4952 | 118.4835 | 119.0876
WHRB#5
Steam Temp. | 331
Steam Pressure | 15.09
Steam Flow | 12.21
Feed water Temp. at Eco. inlet | 130
Feed water Temp. at Eco. Out let | 160
Feed water press. | 25 to 26 kg/cm²
Enthalpy of Steam (kcal/kg) | 743
Enthalpy of Feed waterat Eco. inlet (kcal/kg) | 131
Enthalpy of Feed water at Eco. Outlet (kcal/kg) | 161
| Duct- 1 | Duct- 2
Flue gas flow( M³/hr) | 371663 | 40858
flue gas density | 0.48 | 0.42
Sp. Heat of flue gas | 0.24 | 0.24
Flue gas temp. °C I/L | 349 | 349
Flue gas temp. °C O/L | 93 | 93
Total heat input in boiler(kcal/hr) | 10960787.8656 | 1054332.5184
heat out from boiler | 11017530
boiler effiency | 91.6972